## JH-FL-40
Nanjing Jinhan Technology Co.,Ltd www.jinhan-tech.com zhangyan@jinhan-tech.com
Air Cooled Industrial Chiller
Model |  |  |  | JH-FL-40
Item
Cooling capacity |  |  | kW | 116
|  |  | 103 kcal/h | 100
Power source |  |  | V/ph/Hz | 380/3/50
Gross power |  |  | kW | 34.7
Rated current |  |  | A | 66
Compressor | Type |  |  | Scroll type
| Power |  | kW | 30.6
Condenser | Type |  |  | Efficient inner fin coil type
| Max. pressure |  |  | 3.5 MPa
| Fan type |  |  | The efficiency and low noise outer rotor fan
Evaporator | Type |  |  | Shell and tube type
| Tank volume |  | L | 300
| Temp. range |  | ℃ | 5-30 Adjustable
| Water flow rate |  | m3/h | 20
|  |  | L/min | 333
| Pipe size |  | DN | 50
| Water Max. pressure |  |  | 1.5 MPa
Pump | Type |  |  | Stainless steel centrifugal type
| Power |  | kW | 1.85
| Head |  | m | 21
Refrigerant | Type |  |  | R22
| Throttling type |  |  | Thermal expansion valve
Protector |  |  |  | Pressure、0verload、Anti-freeze、Delay、Over-temperature、Flow
Noise lever |  |  | dB(A) | 69
Unit weight |  |  | kg | 1100
Running weight |  |  | kg | 1200
Dim. |  | L*W*H | mm | 2200*1200*1880
The above cooling capacity is based on the ambient temperature 35℃, the outlet 7℃.