## JH-SL-3
Nanjing Jinhan Technology Co.,Ltd www.jinhan-tech.com zhangyan@jinhan-tech.com
Water Cooled Industrial Chiller
Model |  |  |  | JH-SL-3
Item
Cooling capacity |  |  | kW | 9.9
|  |  | 103 kcal/h | 8..5
Power source |  |  | V/ph/Hz | 380/3/50
Gross power |  |  | kW | 2.7
Rated current |  |  | A | 5.9
Compressor | Type |  |  | Scroll type
| Power |  | kW | 2.3
Condenser | Type |  |  | Shell and tube type
| Max. pressure |  |  | 1.6MPa
| Water flow rate |  | m3/h | 2.1
|  |  | L/min | 35
Evaporator | Type |  |  | Shell and tube type
| Tank volume |  | L | 60
| Temp. range |  | ℃ | 5-30 Adjustable
| Water flow rate |  | m3/h | 1.7
|  |  | L/min | 28.5
| Pipe size |  | DN | 25
Pump | Type |  |  | Stainless steel centrifugal type
| Power |  | kW | 0.37
| Head |  | m | 25
Refrigerant | Type |  |  | R22
| Throttling type |  |  | Thermal expansion valve
Protector |  |  |  | Pressure、Overload、Anti-freeze、Delay、Over-temperature、Flow
Noise lever |  |  | dB(A) | 55
Unit weight |  |  | kg | 120
Dim. |  | L*W*H | mm | 850*720*1265
The above cooling capacity is based on the cooled water inlet temp 30℃, the outlet 35℃, the freeze water inlet temp 7℃.