## JH-SL-30
Nanjing Jinhan Technology Co.,Ltd www.jinhan-tech.com zhangyan@jinhan-tech.com
Water Cooled Industrial Chiller
Model |  |  |  | JH-SL-30
Item
Cooling capacity |  |  | kW | 96
|  |  | 103 kcal/h | 82.6
Power source |  |  | V/ph/Hz | 380/3/50
Gross power |  |  | kW | 22.5
Rated current |  |  | A | 43
Compressor | Type |  |  | Scroll type
| Power |  | kW | 20.2
Condenser | Type |  |  | Shell and tube type
| Max. pressure |  |  | 1.6MPa
| Water flow rate |  | m3/h | 20.6
|  |  | L/min | 344
Evaporator | Type |  |  | Shell and tube type
| Tank volume |  | L | 230
| Temp. range |  | ℃ | 5-30 Adjustable
| Water flow rate |  | m3/h | 16.5
|  |  | L/min | 275
| Pipe size |  | DN | 50
Pump | Type |  |  | Stainless steel centrifugal type
| Power |  | kW | 1.5
| Head |  | m | 20
Refrigerant | Type |  |  | R22
| Throttling type |  |  | Thermal expansion valve
Protector |  |  |  | Pressure、Overload、Anti-freeze、Delay、Over-temperature、Flow
Noise lever |  |  | dB(A) | 64
Unit weight |  |  | kg | 820
Dim. |  | L*W*H | mm | 2080*1050*1570
The above cooling capacity is based on the cooled water inlet temp 30℃, the outlet 35℃, the freeze water inlet temp 7℃.