## ICW-40
Nanjing Jinhan Technology Co.,Ltd www.jinhan-tech.com zhangyan@jinhan-tech.com
Water Cooled Industrial Chiller
Model |  |  |  | JH-SL-40
Item
Cooling capacity |  |  | kW | 128
|  |  | 103 kcal/h | 110
Power source |  |  | V/ph/Hz | 380/3/50
Gross power |  |  | kW | 27.4
Rated current |  |  | A | 55
Compressor | Type |  |  | Scroll type
| Power |  | kW | 25.2
Condenser | Type |  |  | Shell and tube type
| Max. pressure |  |  | 1.6MPa
| Water flow rate |  | m3/h | 27.5
|  |  | L/min | 458
Evaporator | Type |  |  | Shell and tube type
| Tank volume |  | L | 300
| Temp. range |  | ℃ | 5-30 Adjustable
| Water flow rate |  | m3/h | 22
|  |  | L/min | 366
| Pipe size |  | DN | 50
Pump | Type |  |  | Stainless steel centrifugal type
| Power |  | kW | 1.85
| Head |  | m | 21
Refrigerant | Type |  |  | R22
| Throttling type |  |  | Thermal expansion valve
Protector |  |  |  | Pressure、Overload、Anti-freeze、Delay、Over-temperature、Flow
Noise lever |  |  | dB(A) | 65
Unit weight |  |  | kg | 1030
Dim. |  | L*W*H | mm | 2200*1200*1570
The above cooling capacity is based on the cooled water inlet temp 30℃, the outlet 35℃, the freeze water inlet temp 7℃.